{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["新增材料设备单价确认表（市场价）医用气体工程"],"not_rendered":{"defined_names":3},"read":"whole","date_system":"1900"}

{"sheet":"新增材料设备单价确认表（市场价）医用气体工程","index":0,"n_rows":43,"n_cols":6,"rows_kept":43,"merged":[[0,0,0,5],[1,0,3,0],[1,1,3,1],[1,2,3,2],[1,3,3,3],[1,4,3,4],[1,5,3,5]]}
["医用气体工程设备设施清单"]
["序号","材料/设备名称","规格、型号","计量\n单位","暂估工程量","报价（元）"]
[]
[]
[1,"医用不锈钢管","1.名称:医用无缝不锈钢管\n2.安装部位:室内\n3.介质:气体\n4.规格、压力等级:φ19*1.5\n5.连接形式:氩弧焊\n6.空气吹扫气压试验气密性试验\n7.管道脱脂","m",{"v":894.3,"d":"894.30"}]
[2,"医用不锈钢管","1.名称:医用无缝不锈钢管\n2.安装部位:室内\n3.介质:气体\n4.规格、压力等级:φ27*2.0\n5.连接形式:氩弧焊\n6.空气吹扫气压试验气密性试验\n7.管道脱脂","m",{"v":1822,"d":"1822.00"}]
[3,"医用不锈钢管","1.名称:医用无缝不锈钢管\n2.安装部位:室内\n3.介质:气体\n4.规格、压力等级:φ38*2.5\n5.连接形式:氩弧焊\n6.空气吹扫气压试验气密性试验\n7.管道脱脂","m",{"v":536.7,"d":"536.70"}]
[4,"医用不锈钢管","1.名称:医用无缝不锈钢管\n2.安装部位:室内\n3.介质:气体\n4.规格、压力等级:φ42*2.0\n5.连接形式:氩弧焊\n6.空气吹扫气压试验气密性试验\n7.管道脱脂","m",{"v":155.8,"d":"155.80"}]
[5,"医用不锈钢管","1.名称:医用无缝不锈钢管\n2.安装部位:室内\n3.介质:气体\n4.规格、压力等级:φ89*3.0\n5.连接形式:氩弧焊\n6.空气吹扫气压试验气密性试验\n7.管道脱脂","m",{"v":98.2,"d":"98.20"}]
[6,"医用不锈钢管","1.名称:医用无缝不锈钢管\n2.安装部位:室内\n3.介质:气体\n4.规格、压力等级:φ114*3.0\n5.连接形式:氩弧焊\n6.空气吹扫气压试验气密性试验\n7.管道脱脂","m",{"v":120,"d":"120.00"}]
[7,"医用储气罐","1.规格：1.0m³\n2.最高工作压力：0.84MPA\n3.材质：碳钢","台",{"v":2,"d":"2.00"}]
[8,"医用负压吸引机组","医用负压吸引机组\n配置说明：\n1、一套三机头（2用1备）；\n2、总抽气量≥840M3/H，功率22.5KW；\n3、带汽水分离器，机械密封，无泄漏，体积小，性能优良，效率高；\n4、系统负压范围：-0.07MPa～-0.04MPa。\n包含以下配置\n1、电控系统\n2、水环泵\n3、机架及共用底板\n4、阻液器\n5、避震喉3个                      \n6、真空表                     \n7、汽水分离器                        \n8、浮控开关                       \n9、阀门组件                       \n10、双金属温度计                       \n11、入口过滤网","套",1]
[9,"医用真空罐","1.1、医用真空罐1台\n1.1.1、有效容积：2m³  \n1.1.2、材质:Q235B","台",1]
[10,"医用负压分气缸","1.名称:负压分气缸\n2.型号、规格:五进二出\n3.（含安全阀、排水阀、压力表）\n4.脱脂处理","台",1]
[11,"管理主机","1、具有功能显示、设置等功能；\n2、两线数据传输，预留扩展接口，可外接电脑等设备；\n3、支持PC端一览表同步，60门一览表；\n4、带分机呼叫指示灯；\n5、与电话机连接后，可实现护士站和病床之间的双向呼叫对讲。\n6、实现病床与医护站传呼对讲;\n7、按呼叫先后优先呼叫对讲原则; \n8、具有呼叫记忆、循环播报呼叫床号功能\n9、系统采用二线制安装，维修方便，稳定可靠; \n10、人性化设计，操作方便，具有多种实用功能；\n11、ARM-M3处理器， 更高的时钟精度，年误差±1分钟内; \n12、支持电子信息看板，集中管理; 支持中英文切换。","套",18]
[12,"通讯主机","1、具有功能显示、设置等功能；\n2、预留扩展接口，可外接分机等设备；\n3、清晰免提通话；\n4、可实现护士站和病床之间的双向呼叫对讲。\n5、实现病床与医护站传呼对讲;\n6、按呼叫先后优先呼叫对讲原则;","套",18]
[13,"床头分机","1、具有呼叫、取消呼叫及对讲功能；\n2、与系统采用总线连接；\n3、广播级通话音质，放音逼真、清晰；\n4、采用在线编码方式，可任意设定号码；\n5、可呼叫系统主机及免提双向对讲；\n6、物理按键呼叫/复位按键； \n7、含手持呼叫器；","个",626]
[14,"卫浴分机","1、紧急呼叫；\n2、紧急呼叫优先提示；\n3、可取消误触发呼叫；\n4、呼叫时， 灯光提示；","个",244]
[15,"走廊信号线","1.名称:呼叫信号线\n2.型号:RVV-2×0.75mm²\n3.材质:铜芯","m",1100]
[16,"入户信号线","1.名称:呼叫信号线\n2.型号:RVV-2×0.5mm²\n3.材质:铜芯","m",7100]
[17,"医用气体汇流排","1.名称：氧气手动汇流排1.20S（10+10）\n2.手动切换.断电不影响供气\n3.全铜结构\n4.带禁油高低压指示表\n5.双回路，带安全阀0","组",1]
[18,"医用氧气分、集汽(水)缸","1.名称:氧气分气缸\n2.型号、规格:三进六出\n3.材质：不锈钢\n4.（含安全阀、排水阀、压力表）\n5.脱脂处理","台",1]
[19,"医用氧气流量计","1.名称:氧气流量计\n2.流量计量程：200～300L/min\n3.250m³/小时","台",{"v":21,"d":"21.00"}]
[20,"医用氧气二级稳压箱","1.名称:二级减压箱\n2.350L/min，双路减压\n3.输出压力：0.4Mpa（可调）","台",{"v":3,"d":"3.00"}]
[21,"医用空气二级稳压箱","1.名称:二级减压箱\n2.350L/min，双路减压\n3.输出压力：0.4Mpa（可调）","台",{"v":18,"d":"18.00"}]
[22,"声光报警器","1.名称:压力监测报警箱\n2.规格:三气、氧气、负压、空气\n3.对病区压力实时监测显示；具有超压、欠压报警功能；","个",{"v":14,"d":"14.00"}]
[23,"声光报警器","1.名称:压力监测报警箱\n2.规格:二气、氧气、负压\n3.对病区压力实时监测显示；具有超压、欠压报警功能；","个",{"v":7,"d":"7.00"}]
[24,"医疗设备带","1.名称:医疗设备带\n2.材质：优质高强度铝合金\n3.尺寸：200*60MM厚度不小于1.5mm\n4.具有三腔结构，实现气、强弱电分离\n5.面板、底板分体组合，便于检修\n6.表面喷塑涂层，颜色可按要求订制","m",{"v":2027.9,"d":"2027.90"}]
[25,"医用铜管","1.名称:医用优质脱脂紫铜管\n2.安装部位:室内\n3.介质:氧气\n4.规格、压力等级:φ8*0.8\n5.连接形式:银焊连接\n6.管道消毒、冲洗 公称直径","m",{"v":4119.3,"d":"4119.30"}]
[26,"医用铜管","1.名称:医用优质脱脂紫铜管\n2.安装部位:室内\n3.介质:氧气\n4.规格、压力等级:φ10*0.8\n5.连接形式:银焊连接\n6.管道消毒、冲洗 公称直径","m",{"v":3181,"d":"3181.00"}]
[27,"医用铜管","1.名称:医用优质脱脂紫铜管\n3.介质:氧气\n4.规格、压力等级:φ12*0.8\n5.连接形式:银焊连接\n6.管道消毒、冲洗 公称直径","m",{"v":556,"d":"556.00"}]
[28,"医用铜管","1.名称:医用优质脱脂紫铜管 \n2.安装部位:室内\n3.介质:氧气\n4.规格、压力等级:φ16*1.0\n5.连接形式:银焊连接\n6.管道消毒、冲洗 公称直径","m",{"v":1483.3,"d":"1483.30"}]
[29,"医用铜管","1.名称:医用优质脱脂紫铜管 \n2.安装部位:室内\n3.介质:氧气\n4.规格、压力等级:φ19*1.2\n5.连接形式:银焊连接\n6.管道消毒、冲洗 公称直径","m",275.05]
[30,"医用螺杆式空压机","1.功率15KW \n2.排气量2.2m³/min\n3.最高工作压力：0.8MPA\n4.噪音52dB","台",2]
[31,"医用冷干机","处理量：2.6m3/min","台",2]
[32,"医用前级过滤器","处理量：2.6m3/min 带自动排水","个",2]
[33,"医用中级过滤器","处理量：2.6m3/min 带自动排水","个",2]
[34,"医用后级过滤器","处理量：2.6m3/min 带自动排水","个",2]
[35,"活性碳过滤器","处理量：2.6m3/min 带自动排水","个",2]
[36,"医用氧气终端","1.国标\n2.具有防插错功能\n3.满足医气标准进行脱脂清洗\n4.符合CE认证\n5.二万次插拔无无泄漏\n6.快速自封插拔式接头，具有防误插功能，高气密性、二次密封、操作简便","个",{"v":716,"d":"716.00"}]
[37,"医用负压终端","1.国标\n2.具有防插错功能\n3.满足医气标准进行脱脂清洗\n4.符合CE认证\n5.二万次插拔无无泄漏\n6.快速自封插拔式接头，具有防误插功能，高气密性、二次密封、操作简便","个",{"v":694,"d":"694.00"}]
[38,"医用空气终端","1.国标\n2.具有防插错功能\n3.满足医气标准进行脱脂清洗\n4.符合CE认证\n5.二万次插拔无无泄漏\n6.快速自封插拔式接头，具有防误插功能，高气密性、二次密封、操作简便","个",{"v":78,"d":"78.00"}]
[39,"医用氧气维修阀","用于设备带氧气终端停气检修","个",{"v":357,"d":"357.00"}]